## Pump and transfer schemes
Investment Code | C55 Portfolio | Short Code | Investment Name | Category | Recommended Alternative | Details
I034386 | WRS 03.06(PR24) WRC process capacity enhancement | AISTST | Aisthorpe WRC Growth PE | Transfer between catchments | AISTST LAUA Transfer between Catchments | The LAUA 2035 growth forecast, suggests a future P.E of 411 at AISTST, which has a current P.E (2021) of 361. Solution to pump the additional flows (50 p.e) to nearby catchment WRC with available headroom (SCAMST).
I034495 | WRS 03.05(PR24) WRC DWF programme (growth driven) | CLIFST | Clifton WRC Growth DWF Capacity | Transfer between catchments | ONS Transfer between catchments | Transfer to Poppyhilll WRC 2.47km based on shortfall in pe of 1691 No new DWF permit required
I034437 | WRS 03.05(PR24) WRC DWF programme (growth driven) | FREEST | Freethorpe WRC Growth DWF Compliance | Pump Away | Freethorpe ONS Pump Away | ONS forecast at 2035 suggests a future DWF of 213 and PE of 1813 Current permitted DWF is 200
I034490 | WRS 03.06(PR24) WRC process capacity enhancement | HANSST | Hanslope WRC Growth PE Capacity | Transfer between catchments | Hanslope ONS Transfer Between Catchments | ONS forecast at 2035 suggests a future PE of 2652. Baseline 2021 PE is 2576. Required capacity is 2652. Solution to pump the additional flows to nearby catchment WRC with available headroom (ASHTST) where there is approx 6,600 PE headroom and minimal growth.
I034503 | WRS 03.05(PR24) WRC DWF programme (growth driven) | LONDST | Londonthorpe WRC Growth DWF Capacity | Transfer between catchments | LAUA Transfer between catchments | LAUA forecast at 2035 suggests a future DWF of 172 Current permitted DWF is 32 Transfer to Marston WRC 6.69km based on shortfall in permitted DWF 140m3/d (772 pe) No new DWF permit required
I034427 | WRS 03.05(PR24) WRC DWF programme (growth driven) | LBUCST | Long Buckby WRC Growth DWF Compliance | Transfer between catchments | LBUCST ONS Transfer between Catchments | The ONS forecasts a future consented DWF of 1615 m3/d and PE of 8645. Solution to pump the additional flows (1327 p.e) to nearby catchment WRC with available headroom (WHILST).
I034507 | WRS 03.05(PR24) WRC DWF programme (growth driven) | LUDFST | Ludford WRC Growth DWF Capacity | Transfer between catchments | ONS Transfer between catchments | LAUA forecast at 2035 suggests a future DWF of 77 Current permitted DWF is 30 Transfer to Donnington WRC 7.76km based on shortfall in permitted DWF 47m3/d (259 pe) No new DWF permit required
I034504 | WRS 03.05(PR24) WRC DWF programme (growth driven) | NSOMST | North Somercotes WRC Growth DWF Capacity | Transfer between catchments | LAUA Transfer between catchments | LAUA forecast at 2035 suggests a future DWF of 249 Current permitted DWF is 220 Transfer to North Cotes WRC km based on shortfall in permitted DWF 220m3/d (106 pe) No new DWF permit required
I034505 | WRS 03.05(PR24) WRC DWF programme (growth driven) | OWMBST | Owmby WRC Growth DWF Capacity | Transfer between catchments | Owmby Transfer between catchments | LAUA forecast at 2035 suggests a future DWF of 135 Current permitted DWF is 116 Transfer to Glentham WRC 3.820km based on shortfall in permitted DWF 19m3/d (105 pe) No new DWF permit required
I034492 | WRS 03.06(PR24) WRC process capacity enhancement | REPMST | Reepham WRC Growth PE Capacity | Pump Away | Reepham ONS Pump away | ONS forecast at 2035 suggests a future PE of 7818. Baseline 2021 PE is . Required capacity is 390pe. Additional PE pumped to Nettleham WRC.
I034430 | WRS 03.05(PR24) WRC DWF programme (growth driven) | STABST | Stanbridgeford WRC Growth DWF Compliance | Transfer between catchments | STABST Transfer between catchments | Solution to pump the additional flows to nearby catchment WRC with available headroom (DUNSST) where there is approx 7,000m3/d DWF headroom and 30,000PE biological treatment headroom. Max pumped flow based on future DWF of 3420m3/d minus current DWF of 2482m3/d (consented used due to previous flow meter error) multiplied by 4 to give peak flow.
I033405 | WRS 03.05(PR24) WRC DWF programme (growth driven) | TUDDST | Tuddenham Growth / DWF Compliance | New process | New WRC (Same site) & Relocate outfall | Rebuild of site for total predicted pe. Relocation of outfall to River Lark where it is assumed a more suitable consent will be possible.